## READ ME
MESCOM SLD TOOL - TOPOLOGY DATA TEMPLATE
Fill in PARENT_ID, SPUR_ID and WAY. Everything else is already populated from 'DTC DETAILS U4.xlsx'.
1. WHAT THIS FILE IS FOR
The GPS rows in the master tell the tool where every DTC, RMU and MUSS sits. They do not say what is connected to what. With points only, the geographical sheet joins them with a minimum spanning tree - a plausible guess that can put a DTC on the wrong lateral, draw a line across a block, or make a spur run through a building.
One connection per node fixes that. Each row in NODES says 'this node is fed from that node'. Read together, the rows are the whole feeder tree: the trunk, every spur, and the order of DTCs along each one.
2. THE SIX RULES
1. One row per physical node. NODE_ID must be unique.
2. Exactly one PARENT_ID per row - the node immediately upstream, towards the MUSS. Only a MUSS row has a blank parent.
3. The parent must already exist in the NODE_ID column. No cycles: following parent links must always end at a MUSS.
4. Power flows FROM the parent TO the node. Do not write the child in the parent's row.
5. SPUR_ID is T for the main run from the MUSS, S1, S2, ... for laterals. Every node on the same lateral carries the same SPUR_ID.
6. WAY is only used when the parent is an RMU. An RMU is a five-way unit - ODin, ODout, VL1, VL2, VL3 - so a child of an RMU must say which way it leaves by. Leave WAY blank everywhere else. A unit need not use all five ways: only ODin is always cabled, and any of the four outgoing ways, ODout included, may be empty.
3. SHEETS
NODES The only mandatory sheet. One row per MUSS, RMU, GOS, pole, DTC and HT service. PARENT_ID is the connection; everything else describes the node.
SPURS Auto-generated register of the laterals found in NODES. Rename them here (e.g. 'Kote Road lateral'); the names are for the drawing, not for the tree.
RMU WAYS One row per way of every RMU, five per unit: ODin, ODout, VL1, VL2, VL3. CONNECTED says whether a cable is actually landed; the four outgoing ways start empty (N), which is normal. Records the normal state and the label of each way. Prefilled from the RMU rows in NODES; it describes the switchgear, it does not carry the connections.
BENDS Optional. Add rows only where a span has to bend round a block instead of running straight from parent to child. SEQ orders the bend points along that one span.
EXAMPLE A small, complete feeder showing exactly how the rows should read. Copy its pattern; do not edit it.
LISTS Dropdown values. Leave hidden.
4. WHAT IS ALREADY FILLED IN
• 119 DTCs, 5 HT services, 2 MUSS and 2 RMU rows, with the coordinates the master holds.
• PARENT_ID is pre-filled from a minimum spanning tree and marked BASIS = INFERRED. Treat it as a first draft to correct, never as surveyed fact.
• Rows with BASIS = UNKNOWN have no usable GPS or are HT/RMU nodes whose tap is not in the workbook. They need a manual parent.
• SPUR_ID is also inferred: the longest path from the MUSS is called T, every branch off it is numbered S1, S2, ...
• RMU WAYS already lists all 10 ways of the 2 RMUs: ODin cabled, the four outgoing ways marked empty. Fill in a way only where a cable really lands.
5. COLOURS
Amber BASIS the parent is inferred - check it
Orange PARENT_ID no parent yet - the node will be left out of the tree
Green BASIS surveyed or read off the existing SLD - trusted
Orange WAY a way is filled in but the node has no parent - it cannot be placed
Grey RMU WAYS an empty way - no cable, nothing to draw
Amber NORMALLY CONNECTED = Y but the switch state is missing
6. WHAT TO DO FIRST
Start with MRS F1 (the largest feeder). Open the hand-drawn SLD beside this file and, for each DTC, correct PARENT_ID to the pole or DTC it actually hangs from. Add the poles you need as new rows (TYPE = POLE, NODE_ID = P-001 ...). Leave pole coordinates blank if you do not have them - the drawing will place the pole on a straight line between its neighbours, which is good enough for the topology.
When NODES is complete, the generator can be extended to draw the real trunk and spurs instead of inferring them. This workbook is the collection format; the reader is the next code step. See docs/TOPOLOGY_DATA_REQUIREMENTS.md for the reasoning and the optional extras.
7. REBUILDING THIS TEMPLATE
python sld_generator.py --topology-template # refuses to overwrite a filled file python sld_generator.py --topology-template --force # discards your edits and rebuilds
Coordinates are decimal degrees. Valid values for this area: lat about 13.9, long about 75.5. A latitude of 3.9 means a dropped leading digit.

## NODES
NODE_ID | TYPE | NAME | FEEDER | LAT | LONG | PARENT_ID | SPUR_ID | WAY | KVA | PHASE | NORMALLY | CONDUCTOR | BASIS | REMARKS
MUSS-MRS | MUSS | 110/11KV MRS MUSS |  | 13.9103 | 75.5959 |  | T | [5 empty] | SOURCE | Root - no parent. Feeds: MRS F1
MUSS-MANDLI | MUSS | 110/11KV MANDLI MUSS |  | 13.9179 | 75.5628 |  | T | [5 empty] | SOURCE | Root - no parent. Feeds: Mandli F22, Mandli F13, Mandli F3
RMU-KOTE-ROAD | RMU | KOTE ROAD RMU | MRS F1 | 13.9305 | 75.5858 | [5 empty] | NC |  | UNKNOWN | 5-way RMU: ODin, ODout, VL1, VL2, VL3 - not all need be used. Set PARENT_ID = the node it is fed from (that link is way ODin); each child names its way in WAY. See the RMU WAYS sheet
RMU-GANGOTHTI-COLLEGE | RMU | GANGOTHTI COLLEGE RMU | MRS F1 | 13.9312 | 75.5827 | [5 empty] | NC |  | UNKNOWN | 5-way RMU: ODin, ODout, VL1, VL2, VL3 - not all need be used. Set PARENT_ID = the node it is fed from (that link is way ODin); each child names its way in WAY. See the RMU WAYS sheet
SCD-01 | DTC | GANESHA TC | MRS F1 | 13.9312 | 75.5858 | SCD-19 | S1 |  | 250 |  |  |  | INFERRED
SCD-02 | DTC | MARIGADDIGE | MRS F1 | 13.9278 | 75.5814 | SCD-102 | T |  | 200 |  |  |  | INFERRED
SCD-03 | DTC | SHIVAJI TC | MRS F1 | 13.9262 | 75.58 | SCD-26 | S5 |  | 250 |  |  |  | INFERRED
SCD-04 | DTC | BESTARA KERI | MRS F1 | 13.9268 | 75.5775 | SCD-65 | T |  | 250 |  |  |  | INFERRED
SCD-14 | DTC | HEALTH OFFICE | MRS F1 | 13.9303 | 75.5822 | SCD-29 | T |  | 250 |  |  |  | INFERRED
SCD-19 | DTC | KOTE HOSTEL | MRS F1 | 13.9307 | 75.5859 | SCD-44 | S1 |  | 250 |  |  |  | INFERRED
SCD-20 | DTC | SCIENCE FIELD | MRS F1 | 13.9316 | 75.5837 | SCD-81 | S2 |  | 100 |  |  |  | INFERRED
SCD-22 | DTC | SAVARKAR NAGARA | MRS F1 | 13.9294 | 75.578 | SCD-31 | T |  | 250 |  |  |  | INFERRED
SCD-23 | DTC | PRATHAP | MRS F1 | 13.9293 | 75.5809 | SCD-87 | T |  | 250 |  |  |  | INFERRED
SCD-24 | DTC | POST OFFICE | MRS F1 | 13.929 | 75.5835 | SCD-102 | S3 |  | 100 |  |  |  | INFERRED
SCD-26 | DTC | BHOOPALAM | MRS F1 | 13.9266 | 75.5807 | SCD-83 | S5 |  | 250 |  |  |  | INFERRED
SCD-27 | DTC | KATTE SRINATH | MRS F1 | 13.9294 | 75.5826 | SCD-14 | T |  | 100 |  |  |  | INFERRED
SCD-28 | DTC | SONA HONDA | MRS F1 | 13.9296 | 75.5757 | SCD-73 | S9 |  | 250 |  |  |  | INFERRED
SCD-29 | DTC | POLICE QUARTRESS | MRS F1 | 13.9307 | 75.5828 | SCD-79 | T |  | 100 |  |  |  | INFERRED
SCD-31 | DTC | VINAYAKA COMPLEX | MRS F1 | 13.9301 | 75.5786 | SCD-38 | T |  | 100 |  |  |  | INFERRED
SCD-34 | DTC | THIRUPALAIAH | MRS F1 | 13.9282 | 75.5782 | SCD-64 | T |  | 250 |  |  |  | INFERRED
SCD-38 | DTC | DEEPAK PETROL BUNK | MRS F1 | 13.9301 | 75.5788 | SCD-113 | T |  | 63 |  |  |  | INFERRED
SCD-39 | DTC | JAIN MANDIR | MRS F1 | 13.9259 | 75.5799 | SCD-61 | S5 |  | 100 |  |  |  | INFERRED
SCD-40 | DTC | TULUJA BHAVANI | MRS F1 | 13.9253 | 75.578 | SCD-75 | T |  | 100 |  |  |  | INFERRED
SCD-42 | DTC | VICTOR D SOUZA | MRS F1 | 13.9298 | 75.5802 | SCD-23 | T |  | 63 |  |  |  | INFERRED
SCD-43 | DTC | BEKKINA KALMATA | MRS F1 | 13.9313 | 75.5874 | SCD-59 | S1 |  | 100 |  |  |  | INFERRED
SCD-44 | DTC | DIST TRAINING COLLEGE | MRS F1 | 13.9303 | 75.5855 | SCD-110 | T |  | 25 |  |  |  | INFERRED
SCD-45 | DTC | ARAVIND MOTORS | MRS F1 | 13.9326 | 75.5836 | SCD-74 | S2 |  | 100 |  |  |  | INFERRED
SCD-46 | DTC | MTC | MRS F1 | 13.9315 | 75.5808 | SCD-51 | S6 |  | 100 |  |  |  | INFERRED
SCD-47 | DTC | KRISHNA CAFÉ | MRS F1 | 13.9311 | 75.58 | SCD-51 | T |  | 100 |  |  |  | INFERRED
SCD-48 | DTC | PARK TC | MRS F1 | 13.9269 | 75.5776 | SCD-04 | S11 |  | 100 |  |  |  | INFERRED | shared coordinate with SCD-106
SCD-50 | DTC | SHARMA VIDIO | MRS F1 | 13.9304 | 75.5849 | SCD-44 | T |  | 100 |  |  |  | INFERRED
SCD-51 | DTC | KASARAVALLI | MRS F1 | 13.9309 | 75.5804 | SCD-97 | T |  | 100 |  |  |  | INFERRED
SCD-52 | DTC | MARUTHI COMPLEX | MRS F1 | 13.9305 | 75.5791 | SCD-47 | T |  | 100 |  |  |  | INFERRED
SCD-53 | DTC | KOUTTONS | MRS F1 | 13.9301 | 75.5775 | SCD-22 | S7 |  | 100 |  |  |  | INFERRED
SCD-59 | DTC | CMC TC | MRS F1 | 13.9315 | 75.587 | SCD-91 | S1 |  | 63 |  |  |  | INFERRED
SCD-61 | DTC | MANJU JAIN | MRS F1 | 13.9259 | 75.5801 | SCD-71 | S5 |  | 63 |  |  |  | INFERRED
SCD-63 | DTC | BEDARAKERI | MRS F1 | 13.9285 | 75.5785 | SCD-64 | S8 |  | 100 |  |  |  | INFERRED
SCD-64 | DTC | YALAKAPPANA KERI | MRS F1 | 13.9285 | 75.5783 | SCD-99 | T |  | 100 |  |  |  | INFERRED
SCD-65 | DTC | SWASTIK SPORTS | MRS F1 | 13.9281 | 75.577 | SCD-34 | T |  | 25 |  |  |  | INFERRED
SCD-68 | DTC | OLD TALLUK OFFICE | MRS F1 | 3.9264 | 75.5808 |  |  |  | 63 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCD-71 | DTC | MAHENDRA KUMAR JAIN | MRS F1 | 13.9259 | 75.5801 | SCD-03 | S5 |  | 63 |  |  |  | INFERRED
SCD-73 | DTC | NARAYANA COMPLEX | MRS F1 | 13.9287 | 75.5768 | SCD-65 | S9 |  | 63 |  |  |  | INFERRED
SCD-74 | DTC | PRABHU | MRS F1 | 13.932 | 75.5837 | SCD-20 | S2 |  | 100 |  |  |  | INFERRED
SCD-75 | DTC | BLUE MAX | MRS F1 | 13.9257 | 75.5774 | SCD-04 | T |  | 63 |  |  |  | INFERRED
SCD-77 | DTC | NAGRAJ | MRS F1 | 13.9281 | 75.5762 | SCD-65 | S10 |  | 100 |  |  |  | INFERRED
SCD-78 | DTC | GAJANANA HEGDE | MRS F1 | 13.9307 | 75.5842 | SCD-85 | T |  | 63 |  |  |  | INFERRED
SCD-79 | DTC | PRAMOD MEHTA | MRS F1 | 13.9307 | 75.5832 | SCD-81 | T |  | 250 |  |  |  | INFERRED
SCD-81 | DTC | SUPERIDENT OF POLICE | MRS F1 | 13.9308 | 75.5834 | SCD-78 | T |  | 100 |  |  |  | INFERRED
SCD-83 | DTC | AMBALAL | MRS F1 | 13.9265 | 75.5809 | SCD-98 | S5 |  | 100 |  |  |  | INFERRED
SCD-85 | DTC | DHINESH KOTARI | MRS F1 | 13.9308 | 75.5848 | SCD-50 | T |  | 100 |  |  |  | INFERRED
SCD-87 | DTC | CHINMAYA MISSION TC | MRS F1 | 13.9288 | 75.5808 | SCD-02 | T |  | 63 |  |  |  | INFERRED
SCD-90 | DTC | VINAYAKA RASTE TC | MRS F1 | 13.926 | 75.5795 | SCD-39 | S5 |  | 100 |  |  |  | INFERRED
SCD-91 | DTC | OBL ROAD MRN NAIDU APARTMENT | MRS F1 | 13.9315 | 75.5862 | SCD-01 | S1 |  | 250 |  |  |  | INFERRED
SCD-92 | DTC | TULUJA BHAVANI CROSS SIYAL COMPLEX | MRS F1 | 13.9254 | 75.5771 | SCD-75 | S12 |  | 100 |  |  |  | INFERRED
SCD-94 | DTC | TRF_OLD TALUK OFFICE | MRS F1 | 13.9264 | 75.5819 | SCD-98 | S5 |  | 63 |  |  |  | INFERRED
SCD-95 | DTC | TRF_KOTE WETWELL BACKSIDE | MRS F1 | 13.9306 | 75.587 | SCD-43 | S1 |  | 63 |  |  |  | INFERRED
SCD-97 | DTC | KASARAVALLI TOWER MAHARAJA ROAD | MRS F1 | 13.9307 | 75.5804 | SCD-42 | T |  | 100 |  |  |  | INFERRED
SCD-98 | DTC | PRAVEENKUMAR MARIKAMBA TEMPLE BACKSIDE | MRS F1 | 13.927 | 75.5815 | SCD-109 | S5 |  | 63 |  |  |  | INFERRED
SCD-99 | DTC | Charmada Mandi TC | MRS F1 | 13.9292 | 75.578 | SCD-22 | T |  | 100 |  |  |  | INFERRED
SCD-100 | DTC | Antharaghtamma Temple TC | MRS F1 | 13.9251 | 75.578 | SCD-40 | T |  | 100 |  |  |  | INFERRED
SCD-101 | DTC | Fish Market TC | MRS F1 | 13.9285 | 75.5786 | SCD-63 | S8 |  | 100 |  |  |  | INFERRED
SCD-102 | DTC | MAHAVEER JAIN SCHOOL KOTE ROAD | MRS F1 | 13.9287 | 75.5827 | SCD-27 | T |  | 63 |  |  |  | INFERRED
SCD-105 | DTC | ShivappaNayaka Aramane TC | MRS F1 | 13.9277 | 75.5832 | SCD-102 | S4 |  | 63 |  |  |  | INFERRED
SCD-106 | DTC | Elerevanna Keri TC | MRS F1 | 13.9269 | 75.5776 | SCD-48 | S11 |  | 100 |  |  |  | INFERRED | shared coordinate with SCD-48
SCD-109 | DTC | Marikamba Temple Backside | MRS F1 | 13.9276 | 75.5813 | SCD-02 | S5 |  | 100 |  |  |  | INFERRED
SCD-110 | DTC | Gayathti Temple Appaji Rao Compound | MRS F1 | 13.9291 | 75.5862 | MUSS-MRS | T |  | 100 |  |  |  | INFERRED
SCD-113 | DTC | DEEPAK PETROL BUNK EV CHARGING STATION | MRS F1 | 13.9305 | 75.579 | SCD-52 | T |  | 100 |  |  |  | INFERRED
HT-28 | HT | SHIMOGA COMPLEX PRIVATE LIMITED | MRS F1 | [5 empty] | 150 |  |  |  | UNKNOWN | No GPS - set PARENT_ID to the tap pole
HT-87 | HT | M/S SHAHI EXPORTS PVT. LTD. | MRS F1 | [5 empty] | 200 |  |  |  | UNKNOWN | No GPS - set PARENT_ID to the tap pole
HT-92 | HT | M/S PAI INTERNATIONAL LTD., | MRS F1 | [5 empty] | 98 |  |  |  | UNKNOWN | No GPS - set PARENT_ID to the tap pole
HT-188 | HT | DISTRICT HEALTH & FAMILY WELFARE OFFICER | MRS F1 | [5 empty] | 70 |  |  |  | UNKNOWN | No GPS - set PARENT_ID to the tap pole
HT-193 | HT | COMISSIONER, KOTE WETWELL | MRS F1 | [5 empty] | 60 |  |  |  | UNKNOWN | No GPS - set PARENT_ID to the tap pole
SCD-06 | DTC | HARALENNE KERI | Mandli F22 | 13.9288 | 75.575 | SCD-41 | T |  | 250 |  |  |  | INFERRED
SCD-07 | DTC | BARMAPPA NAGARA | Mandli F22 | 13.9265 | 75.5738 | SCD-57 | T |  | 250 |  |  |  | INFERRED
SCD-12 | DTC | JAYANTHI | Mandli F22 | 13.9255 | 75.5708 | MUSS-MANDLI | T |  | 250 |  |  |  | INFERRED
SCD-13 | DTC | BHAVANI SINGH | Mandli F22 | 13.9292 | 75.5765 | SCD-15 | S6 |  | 63 |  |  |  | INFERRED
SCD-15 | DTC | CHINNA BELLI | Mandli F22 | 13.9295 | 75.5764 | SCD-58 | T |  | 250 |  |  |  | INFERRED
SCD-17 | DTC | PANCHATARA | Mandli F22 | 13.9293 | 75.5752 | SCD-06 | T |  | 250 |  |  |  | INFERRED
SCD-21 | DTC | ABDUL AZEEZ | Mandli F22 | 13.9279 | 75.575 | SCD-80 | T |  | 63 |  |  |  | INFERRED
SCD-32 | DTC | BARMAPPA NAGARA | Mandli F22 | 13.9273 | 75.5733 | SCD-07 | S2 |  | 100 |  |  |  | INFERRED
SCD-37 | DTC | JAMIYA MASEEDI | Mandli F22 | 13.9271 | 75.5759 | SCD-104 | T |  | 250 |  |  |  | INFERRED
SCD-41 | DTC | KASTURBA | Mandli F22 | 13.9288 | 75.5752 | SCD-89 | T |  | 250 |  |  |  | INFERRED
SCD-54 | DTC | DOUBLE ROAD | Mandli F22 | 13.9301 | 75.5769 | SCD-56 | T |  | 100 |  |  |  | INFERRED
SCD-55 | DTC | GANDHI BAZAR UNDER PASS | Mandli F22 | 13.9298 | 75.5753 | SCD-17 | T |  | 250 |  |  |  | INFERRED
SCD-56 | DTC | GANGA MEDICAL | Mandli F22 | 13.9299 | 75.5769 | SCD-15 | T |  | 100 |  |  |  | INFERRED
SCD-57 | DTC | MS TOWER | Mandli F22 | 13.9262 | 75.5732 | SCD-107 | T |  | 100 |  |  |  | INFERRED
SCD-58 | DTC | AMBIKA PAPER | Mandli F22 | 13.9294 | 75.5761 | SCD-55 | T |  | 63 |  |  |  | INFERRED
SCD-60 | DTC | UPPAR KERI | Mandli F22 | 13.9269 | 75.5755 | SCD-66 | T |  | 100 |  |  |  | INFERRED
SCD-62 | DTC | SHIMOGA BANGLES | Mandli F22 | 13.927 | 75.5762 | SCD-37 | S4 |  | 100 |  |  |  | INFERRED
SCD-66 | DTC | BASANNI HOTEL | Mandli F22 | 13.9263 | 75.5748 | SCD-07 | T |  | 100 |  |  |  | INFERRED
SCD-70 | DTC | GAYATRI SCHOOL | Mandli F22 | 13.9252 | 75.575 | SCD-66 | S3 |  | 63 |  |  |  | INFERRED
SCD-80 | DTC | MAHENDRA KUMAR | Mandli F22 | 13.9279 | 75.5755 | SCD-37 | T |  | 100 |  |  |  | INFERRED
SCD-84 | DTC | BALEGUNDI KR PURAM ROAD | Mandli F22 | 13.9254 | 75.5729 | SCD-107 | S1 |  | 100 |  |  |  | INFERRED
SCD-86 | DTC | SHAKTI GANAPATHI TC | Mandli F22 | 13.9249 | 75.573 | SCD-84 | S1 |  | 63 |  |  |  | INFERRED
SCD-88 | DTC | KR PURAM SCHOOL TC | Mandli F22 | 13.9261 | 75.5724 | SCD-12 | T |  | 100 |  |  |  | INFERRED
SCD-89 | DTC | CHAPPALI ANGADI ROAD TC | Mandli F22 | 13.9283 | 75.575 | SCD-21 | T |  | 100 |  |  |  | INFERRED
SCF-94 | DTC | KashiBai Apartment | Mandli F22 | [5 empty] | 250 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCD-104 | DTC | AnanthaLeela Upparkeri | Mandli F22 | 13.9269 | 75.5758 | SCD-60 | T |  | 100 |  |  |  | INFERRED
SCD-107 | DTC | Balegundi Conservancy | Mandli F22 | 13.9257 | 75.5726 | SCD-88 | T |  | 100 |  |  |  | INFERRED
SCD-108 | DTC | Gayathri School Compound | Mandli F22 | 13.9252 | 75.5751 | SCD-70 | S3 |  | 100 |  |  |  | INFERRED
SCD-111 | DTC | SUBRAMANYA MKK ROAD MSB TC | Mandli F22 | 13.929 | 75.5745 | SCD-06 | S5 |  | 63 |  |  |  | INFERRED
SCD-112 | DTC | VINAY MKK ROAD MSB TC | Mandli F22 | 13.9291 | 75.5745 | SCD-111 | S5 |  | 63 |  |  |  | INFERRED
SCF-112 | DTC | Pradeep Kumar | Mandli F22 | [5 empty] | 63 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCF-140 | DTC | KIRAN MEDICAL KR PURAM | Mandli F22 | [5 empty] | 100 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCF-03 | DTC | RAVIVARMA BEDI | Mandli F13 | [5 empty] | 250 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCD-05 | DTC | HAVINA KERI | Mandli F13 | 13.9247 | 75.5778 | SCD-76 | S3 |  | 250 |  |  |  | INFERRED
SCF-05 | DTC | VANDANA TALKIES | Mandli F13 | [5 empty] | 250 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCD-08 | DTC | OLD VEGETABLE | Mandli F13 | 13.9241 | 75.577 | SCD-35 | T |  | 250 |  |  |  | INFERRED
SCD-09 | DTC | MANJUNATHA TALKIES | Mandli F13 | 13.9235 | 75.5754 | SCD-11 | S1 |  | 200 |  |  |  | INFERRED
SCD-10 | DTC | KUMBARGUNDI | Mandli F13 | 13.9228 | 75.5771 | SCD-11 | T |  | 250 |  |  |  | INFERRED
SCD-11 | DTC | JPN SCHOOL | Mandli F13 | 13.9225 | 75.5756 | MUSS-MANDLI | T |  | 63 |  |  |  | INFERRED
SCD-16 | DTC | CHOR BAZAR | Mandli F13 | 13.9247 | 75.5765 | SCD-30 | T |  | 100 |  |  |  | INFERRED
SCD-25 | DTC | H SIDDAIAH | Mandli F13 | 13.925 | 75.5754 | SCD-49 | T |  | 250 |  |  |  | INFERRED
SCD-30 | DTC | RATHAN CHAND | Mandli F13 | 13.9242 | 75.5769 | SCD-08 | T |  | 25 |  |  |  | INFERRED
SCD-35 | DTC | KUMBARGUNDI | Mandli F13 | 13.9239 | 75.5772 | SCD-10 | T |  | 100 |  |  |  | INFERRED
SCD-36 | DTC | RELIANCE KUMBARGUNDI | Mandli F13 | 13.924 | 75.5774 | SCD-35 | S3 |  | 100 |  |  |  | INFERRED
SCD-49 | DTC | KANCHAN TEXTTILE | Mandli F13 | 13.9254 | 75.5762 | SCD-67 | T |  | 100 |  |  |  | INFERRED
SCD-67 | DTC | NAVIN BED CENTRE | Mandli F13 | 13.9252 | 75.5765 | SCD-16 | T |  | 100 |  |  |  | INFERRED
SCD-69 | DTC | KISHOR KUMAR | Mandli F13 | 13.9249 | 75.5787 | SCD-76 | S3 |  | 63 |  |  |  | INFERRED
SCD-72 | DTC | BHAGAVAN JAIN | Mandli F13 | 13.9228 | 75.5775 | SCD-10 | S2 |  | 100 |  |  |  | INFERRED
SCD-76 | DTC | HARISH KUMAR | Mandli F13 | 13.9247 | 75.5779 | SCD-103 | S3 |  | 63 |  |  |  | INFERRED
SCD-93 | DTC | TRF_RAMANNASHETTY PARK | Mandli F13 | 13.9236 | 75.5783 | SCD-103 | S3 |  | 63 |  |  |  | INFERRED
SCD-103 | DTC | Bhavasaara Kshatriya Ramanna Shetty Park | Mandli F13 | 13.9244 | 75.578 | SCD-36 | S3 |  | 63 |  |  |  | INFERRED
SCE-03 | DTC | AGRICULTURE OFFICE OT ROAD | Mandli F3 | [5 empty] | 250 |  |  |  | UNKNOWN | no usable GPS - set PARENT_ID by hand
SCD-18 | DTC | OT ROAD | Mandli F3 | 13.9275 | 75.5724 | MUSS-MANDLI | T |  | 250 |  |  |  | INFERRED
SCD-33 | DTC | KR PURAM | Mandli F3 | 13.9278 | 75.5729 | SCD-18 | T |  | 250 |  |  |  | INFERRED
SCD-82 | DTC | BHARATH OT ROAD | Mandli F3 | 13.9282 | 75.5729 | SCD-33 | T |  | 63 |  |  |  | INFERRED
SCD-96 | DTC | PALLAVI HOTEL | Mandli F3 | 13.9289 | 75.5741 | SCD-82 | T |  | 100 |  |  |  | INFERRED

## SPURS
FEEDER | SPUR_ID | LABEL | FROM_NODE | IS_TRUNK | DTC_COUNT | KVA_TOTAL | NOTES
MRS F1 | T | Main line from MUSS | MUSS-MRS | Y | 31 | 3728 | Longest path from the MUSS - rename if the real trunk is another run
MRS F1 | S1 |  | SCD-44 | N | 6 | 976
MRS F1 | S2 |  | SCD-81 | N | 3 | 300
MRS F1 | S3 |  | SCD-102 | N | 1 | 100
MRS F1 | S4 |  | SCD-102 | N | 1 | 63
MRS F1 | S5 |  | SCD-02 | N | 10 | 1152
MRS F1 | S6 |  | SCD-51 | N | 1 | 100
MRS F1 | S7 |  | SCD-22 | N | 1 | 100
MRS F1 | S8 |  | SCD-64 | N | 2 | 200
MRS F1 | S9 |  | SCD-65 | N | 2 | 313
MRS F1 | S10 |  | SCD-65 | N | 1 | 100
MRS F1 | S11 |  | SCD-04 | N | 2 | 200
MRS F1 | S12 |  | SCD-75 | N | 1 | 100
Mandli F22 | T | Main line from MUSS | MUSS-MANDLI | Y | 20 | 3126 | Longest path from the MUSS - rename if the real trunk is another run
Mandli F22 | S1 |  | SCD-107 | N | 2 | 163
Mandli F22 | S2 |  | SCD-07 | N | 1 | 100
Mandli F22 | S3 |  | SCD-66 | N | 2 | 163
Mandli F22 | S4 |  | SCD-37 | N | 1 | 100
Mandli F22 | S5 |  | SCD-06 | N | 2 | 126
Mandli F22 | S6 |  | SCD-15 | N | 1 | 63
Mandli F13 | T | Main line from MUSS | MUSS-MANDLI | Y | 9 | 1238 | Longest path from the MUSS - rename if the real trunk is another run
Mandli F13 | S1 |  | SCD-11 | N | 1 | 200
Mandli F13 | S2 |  | SCD-10 | N | 1 | 100
Mandli F13 | S3 |  | SCD-35 | N | 6 | 602
Mandli F3 | T | Main line from MUSS | MUSS-MANDLI | Y | 4 | 663 | Longest path from the MUSS - rename if the real trunk is another run

## RMU WAYS
RMU_ID | WAY | DIRECTION | CONNECTED | NORMALLY | LABEL | NOTES
RMU-KOTE-ROAD | ODin | IN | Y | NC |  | Incoming way, always cabled - the RMU's own PARENT_ID is this link
RMU-KOTE-ROAD | ODout | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-KOTE-ROAD | VL1 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-KOTE-ROAD | VL2 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-KOTE-ROAD | VL3 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-GANGOTHTI-COLLEGE | ODin | IN | Y | NC |  | Incoming way, always cabled - the RMU's own PARENT_ID is this link
RMU-GANGOTHTI-COLLEGE | ODout | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-GANGOTHTI-COLLEGE | VL1 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-GANGOTHTI-COLLEGE | VL2 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY
RMU-GANGOTHTI-COLLEGE | VL3 | OUT | N |  |  | Empty is normal: set CONNECTED = Y only when a cable is landed and a child row names this way in NODES!WAY

## BENDS
FROM_ID | TO_ID | SEQ | LAT | LONG | NOTES
Add one row per bend on a span, SEQ = 1, 2, 3 ... along the line.

## EXAMPLE
EXAMPLE - a small feeder, filled in the required format
The trunk runs MUSS -> P-001 -> GOS-01 -> P-002 -> RMU (way ODin) -> P-003 (way VL2). SCD-08 leaves the RMU by way VL1; ODout and VL3 are empty. SCD-01 taps P-001. Spur S1 leaves the trunk at P-002 and feeds SCD-07. Every row's PARENT_ID points upstream; SPUR_ID groups the branch and WAY names the RMU way a child leaves by.
NODE_ID | TYPE | NAME | FEEDER | LAT | LONG | PARENT_ID | SPUR_ID | WAY | KVA | PHASE | NORMALLY | CONDUCTOR | BASIS | REMARKS
MUSS-DEMO | MUSS | 110/11KV DEMO MUSS | DEMO | 13.93 | 75.585 |  | T | [5 empty] | SURVEYED | Root - no parent
P-001 | POLE | Pole 1 | DEMO | 13.9298 | 75.5848 | MUSS-DEMO | T |  |  |  |  | 3x95 ABC | SURVEYED
GOS-01 | GOS | DEMO GOS | DEMO | 13.9296 | 75.5846 | P-001 | T |  |  |  | NC | 3x95 ABC | SURVEYED | Normally closed
SCD-01 | DTC | GANESHA TC | DEMO | 13.9296 | 75.5845 | P-001 | T |  | 250 | 3PH |  | 3x25 ABC | SURVEYED | Tap off P-001, 30 m service
P-002 | POLE | Pole 2 | DEMO | 13.9293 | 75.5843 | GOS-01 | T |  |  |  |  | 3x95 ABC | SURVEYED | Branch point for S1
P-010 | POLE | Branch pole | DEMO | 13.9292 | 75.5842 | P-002 | S1 |  |  |  |  | 3x95 ABC | SURVEYED | First pole of spur S1
SCD-07 | DTC | TEMPLE STREET | DEMO | 13.9292 | 75.5842 | P-010 | S1 |  | 63 | 3PH |  | 3x25 ABC | SURVEYED
RMU-DEMO | RMU | DEMO RMU | DEMO | 13.9293 | 75.5844 | P-002 | T |  |  |  | NC | 3x95 ABC | SURVEYED | 5-way unit. Fed from P-002 - that link is way ODin
P-003 | POLE | Pole 3 | DEMO | 13.929 | 75.584 | RMU-DEMO | T | VL2 |  |  |  | 3x95 ABC | SURVEYED | Continues beyond the RMU by way VL2 - the run out is not always ODout
SCD-08 | DTC | SCHOOL | DEMO | 13.9294 | 75.5843 | RMU-DEMO | T | VL1 | 100 | 3PH |  | 3x25 ABC | SURVEYED | Tapped off RMU way VL1
BENDS - optional shape points for one span
FROM_ID | TO_ID | SEQ | LAT | LONG | NOTES
P-001 | P-002 | 1 | 13.9297 | 75.5849 | Line turns at the school corner
P-001 | P-002 | 2 | 13.9295 | 75.5847 | Then runs along the compound wall
RMU WAYS - the five ways of DEMO RMU, as listed on the RMU WAYS sheet
RMU_ID | WAY | DIRECTION | CONNECTED | NORMALLY | LABEL | NOTES
RMU-DEMO | ODin | IN | Y | NC | In from P-002 | Fed from P-002; no child row names this way
RMU-DEMO | ODout | OUT | N |  |  | Empty - no cable landed on this way
RMU-DEMO | VL1 | OUT | Y | NC |  | SCD-08 carries WAY = VL1
RMU-DEMO | VL2 | OUT | Y | NC | Out to P-003 | P-003 carries WAY = VL2; the continuing run is not always ODout
RMU-DEMO | VL3 | OUT | N |  | Spare | Empty spare way, ready for a new cable

## LISTS (hidden)
TYPE | PHASE | NORMALLY | BASIS | WAY_ALL | WAY_CHILD | DIRECTION | YES_NO
MUSS | 3PH | NC | SOURCE | ODin | ODout | IN | Y
RMU | 1PH | NO | INFERRED | ODout | VL1 | OUT | N
GOS |  |  | SURVEYED | VL1 | VL2
POLE |  |  | FROM-SLD | VL2 | VL3
DTC |  |  | UNKNOWN | VL3
HT
FUSE
LA
JUNCTION